TYPE 3

1) Recovery machines using water as the condensing medium would generally use the?

a) cooling tower water

b) municipal water supply

c) condensate water

d) ice water

2) Frost would be best removed from a site glass by?

a) reversing the cycle

b) chip the ice off

c) spraying with alcohol

d) turn the water supply off

3) Recovery cylinders are color coded?

a) yellow with grey tops

b) grey with yellow tops

c) yellow with white tops

d) purple

4) Which refrigerant is a CFC and has been used with low pressure appliances?

a) R-11

b) R-12

c) R-22

d) R-500

5) Type 3 certification as classified by EPA is for?

a) small appliances

b) high and very high pressure appliances

c) low pressure appliances

d) none of the above

6) The maximum pressure that should be applied to a low pressure chiller when leak checking with controlled nitrogen is?

a) 3 psig

b) 10 psig

c) 20 psig

d) 30 psig

7) The short term replacement refrigerant for R-11 chillers is?

a) R-22

b) R-123

c) R-500

d) nitrogen

8) Water tube leaks in a low pressure chiller are usually found with?

a) water puddles

b) frosted coils

c) hydrostatic tube test

d) leak detector

9) The required evacuation level for recovering refrigerant from a low pressure appliance with a recovery machine manufactured before November 15, 1993 is?

a) 0 psig

b) 4 inches Hg

c) 10 inches Hg

d) 25 inches Hg

10) The required evacuation level for recovering refrigerant from a low pressure appliance with a recovery machine after November 15, 1993 is?

a) 10 inches Hg

b) 25 mm Hg absolute

c) 29 inches Hg

d) 25 inches Hg

11) A low pressure chiller generally has a rupture disc set at?

a) 3 psig

b) 8 psig

c) 10 psig

d) 15 psig

12) To prevent freezing of the water coils of a low pressure chiller it is recommended that?

a) when charging, begin with vapor phase

b) circulate water through the chiller

c) do not inject liquid during charging until saturation temperature is above 32 F

d) all of the above

13) A low pressure chiller providing comfort cooling that has an annual leak rate of _______ % of the total charge must be repaired?

a) 15

b) 20

c) 35

d) 50

14) R-134a is classified as a _____ under ASHRAE 34 standard safety group?

a) A1

b) A2

c) B1

d) B2

15) Under ASHRAE standard 15, what refrigerant requires equipment room sensors?

a) R-12

b) R-500

c) R-123

d) R-134a

16) Under ASHRAE standard 15, the following refrigerants require equipment room oxygen deprivation sensors?

a) R-11

b) R-12

c) R-134a

d) all of the above

17) Low pressure chillers required purged units because?

a) they operate below atmospheric pressure

b) they draw non condensable through gaskets and seals

c) both a and b

d) they don’t require purged units

18) The rupture disc of a low pressure chiller is connected to the?

a) high side

b) low side

c) compressor

d) purged valve

19) The purged unit draws from the?

a) top of the condenser

b) suction of the compressor

c) evaporator

d) rupture disc

20) Before a low pressure appliance is dismantled and salvaged?

a) the refrigerant must be recovered

b) file recovery forms

c) reclaim the refrigerant

d) vent the refrigerant

21) machine room safety standards have been established by?

a) ARI-7000

b) ARI-740

c) ASHRAE 34

d) ASHRAE 15

22) Refrigerant vapor is charged into a low pressure chiller initially to prevent?

a) safety shutdown

b) water freeze up caused by system vacuum

c) quicker

d) never charge vapor into a chiller

23) If excessive nitrogen pressure is excreted within a low pressure chiller what component would fail first?

a) evaporator coil

b) rupture disc

c) compressor seals

d) cooling tower

24) R-11 and R-123 refrigerants are?

a) oxygen depleting

b) heavier than air

c) are class 1 and 2 substances as defined by EPA

d) all of the above

25) R-11 is a?

a) CFC

b) HCFC

c) HFC

d) none of the above

26) When leak testing a low pressure chiller the maximum test pressure should be?

a) 5 psig

b) 10 psig

c) 15 psig

d) 20 psig

27) The rupture disc on a chiller is generally set for?

a) 5 psig

b) 10 psig

c) 15 psig

d) 20 psig

28) EPA’s required evacuation level for a low pressure appliance using equipment manufactured before November 15, 1993 is?

a) 25 inches Hg vacuum

b) 27 inches Hg vacuum

c) 15 inches Hg vacuum

d) 25 mm Hg absolute

29) EPA’s required evacuation level for a low pressure appliance using equipment manufactured after November 15, 1993 is?

a) 25 inches Hg vacuum

b) 27 inches Hg vacuum

c) 15 inches Hg vacuum

d) 25 mm Hg absolute

30) Air entering the refrigerant in a low pressure chiller is always a concern       because?

a) low pressure chillers can operate at pressures below atmospheric

b) low pressure chillers operate at pressures above atmospheric

c) air has an affinity for R-11

d) a chillers purged unit constantly takes in air

31)  When using nitrogen with a pressure over 10 psig, which component could fail?

a) rupture disc

b) purged unit

c) condenser tubes

d) evaporator tubes

32) Water should be circulated through the chiller during recovery because it will?

a) lower the chiller vacuum

b) prevent freeze up

c) test the pump

d) ensure less contamination

33) What does 25mm Hg absolute equal?

a) 25 inches Hg vacuum

b) 29 inches Hg vacuum

c) 30 inches Hg vacuum

d) 1500 microns

34) If a chiller providing comfort cooling has a leak rate of _______ or more, it must be repaired?

a) 35%

b) 25%

c) 15%

d) 10%

35) _______ of equipment with charges of 50lbs or more, must keep records of refrigerant added during service and maintenance?

a) owners

b) installers

c) technicians

d) certified technicians

36) R-134a is a group _______ refrigerant; R-123 is a group _______ refrigerant?

a) A1, A1

b) B1, B1

c) A1, B1

d) B1, A1

37)  Low pressure chillers use purge units because?

a) oil must be removed from the evaporator

b) refrigerant pressures get too high on a warm day

c) EPA now requires a purge unit

d) low pressure chillers operate below atmospheric pressure

38) There are no exceptions to the required evacuation levels established by EPA?

a) true

b) false

39) At all times a system should be protected by a?

a) low pressure control

b) high pressure control

c) pressure limiting device

d) king valve

40) Heating the recovery container during charging will result in?

a) faster vapor transfer

b) slower moving liquid

c) nothing that will affect the process

d) a slower charging process

41) According to EPA, type 3 certification is necessary for servicing small appliances?

a) true

b) false

42) R-11 at a pressure of 18.1 inches Hg vacuum has a temperature of?

a) 30 F

b) 32 F

c) 34 F

d) 36 F