| 76. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Recovery machines using water as the condensing medium would generally use: a.; cooling tower water; c.; condensate water. b.; municipal water supply; d.; ice water. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 77. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Frost is best removed from a sight glass by: a.; reversing the cycle; c.; spraying with alcohol. b.; chip the ice off; d.; turn the water supply off. |
| 78. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Recovery cylinders are color coded: a.; yellow with gray tops; c.; yellow with white tops. b.; gray with yellow tops; d.; White. |
| 79. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Which refrigerant is a CFC and has been used with low pressure appliances? a.; R-11; c.; R-22. b.; R-12; d.; R-500. |
| 80. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Type III certification as classified by the EPA is for: a.; small appliances; c.; low pressure appliances. b.; high and very high pressure appliances; d.; none of the above. |
| 81. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | The maximum pressure that should be applied to a low pressure chiller when leak checking with controlled nitrogen is ___ PSIG. a.; 3; c.; 20. b.; 10; d.; 30. |
| 82. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | The short term replacement for R-11 refrigerant in chillers is: a.; R-22; c.; R-50. b.; R-123; d.; Nitrogen. |
| 84. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | The required evacuation level for recovering refrigerant from a low pressure appliance with a recovery machine manufactured before November 15, 1993 is: a.; 0 PSIG; c.; 10” HG. b.; 4” HG; d.; 25 “ HG. |
| 85. |  |  |  |  |  |  |  |  |  |  |  |  |  |  | The required evacuation level for recovering refrigerant from a low pressure appliance with a recovery machine manufactured after November 15, 1993 is: a.; 0 mm; c.; 10 mm HG. b.; 4mm HG; d.; 25 mm HG. |
| 86. |  |  |  |  |  |  |  |  |  |  |  |  |  | A low pressure chiller generally has the rupture disk set at ___ PSIG. a.; 3; c.; 10. b.; 8; d.; 15. |
| 87. |  |  |  |  |  |  |  |  |  |  |  |  | To prevent freezing of the water coils of a low pressure chiller, it is recommended that: a.; when charging, begin with vapor; c.; do not charge liquid until saturation temperature is above 32°F. b.; circulate water through the chiller when charging; d.; all of the above. |
| 88. |  |  |  |  |  |  |  |  |  |  |  | A low pressure chiller that provides comfort cooling that has an annual leak rate of ____% of the total charge, must be repaired. a.; 15; c.; 35. b.; 20; d.; 50. |
| 89. |  |  |  |  |  |  |  |  |  |  | R-134a is classified as a ____ under ASHRAE 34 Standard Safety Group: a.; A1; c.; B1. b.; A2; d.; B2. |
| 90. |  |  |  |  |  |  |  |  |  | R-123 is classified as a ____ under ASHRAE 34 Standard Safety Group: a.; A1; c.; B1. b.; A2; d.; B2. |
| 91. |  |  |  |  |  |  |  |  | Under ASHRAE Standard 15, what refrigerant requires equipment room sensors? a.; R-12; c.; r-123. b.; R-500; d.; r-134a. |
| 92. |  |  |  |  |  |  |  | Under ASHRAE Standard 15, what refrigerant requires equipment room oxygen deprivation sensors? a.; R-12; c.; R-134a. b.; R-500; d.; all of the above. |
| 93. |  |  |  |  |  |  | Low pressure chillers require purge units because: a.; they operate below atmospheric pressure; c.; A & B. b.; they draw non-condensables through gaskets and seals; d.; they do not require purge units. |
| 94. |  |  |  |  |  | The rupture disk of a low pressure chiller is connected to the a.; high side; c.; compressor. b.; low side; d.; purge valve. |
| 95. |  |  |  |  | The purge unit usually draws from the a.; top of the condenser; c.; evaporator. b.; suction of the compressor; d.; rupture disk. |
| 96. |  |  |  |  | Before a low pressure appliance is dismantled and salvaged a.; the refrigerant must be recovered; c.; reclaim the refrigerant. b.; file recovery forms; d.; vent the refrigerant. |
| 97. |  |  |  | Machine room safety standards have been established by a.; ARI-7000; c.; ASHRAE-34. b.; ARI-740; d.; ASHRAE-15. |
| 98. |  | Refrigerant vapor is charged into a low pressure chiller initially to prevent a.; safety shut down; c.; quicker. b.; water freeze up caused by system vacuum; d.; never charge vapor into a chiller. |
| 99. | If excessive nitrogen pressure is exerted within a low pressure chiller, what component would fail first a.; evaporator coil; c.; compressor seals. b.; rupture disk; d.; cooling tower. |
| 100. |  |  | R-11 & R-123 refrigerants are a.; oxygen depleting; c.; are Class I and II substances as defined by the EPA. b.; heavier than air; d.; all of the above. |